## Slide 1: Intensifying Treatment and Resource Recovery SWIFTly and Pragmatically at HRSD
Charles B. Bott, PhD, PE, BCEE
Chief Technical Officer &
Director of Water Technology and Research
Hampton Roads Sanitation District

## Slide 2
Provide wastewater treatment for 18 localities (~250 MGD treatment capacity)
Serve 1.7 million people (20% of all Virginians)
Independent political subdivision with Governor appointed Commission
Who/What is HRSD?
HRSD Treatment Facilities
Notes: HRSD provides wastewater treatment for 18 localities, recently adding in Surry County services to the fold. We serve a population of about 1.7 million people which is about 1/5 of the population of Virginia. One unique aspect of our organization is that we are a true regional entity and are not controlled by any one jurisdiction. As an independent political subdivision oversight is provided by Governor appointed Commissioners. We own and operate 13 facilities with a combined capacity of roughly 250 MGD. The facility locations are denoted by the yellow diamonds. The SWIFT facilities are those located along the James and the lower York River – 7 facilities in all. One other note of importance to the discussion is that storm and sewer are separate systems and each of the Hampton Roads communities manages its own stormwater program.

## Slide 3: Water Issues Challenging Virginia and Hampton Roads
Depletion of groundwater resources
  Including protection from saltwater contamination
Water quality concerns
  Chesapeake Bay restoration (N & P removal)
  Local water quality issues
Sea level rise
  Compounded by land subsidence
Wet weather sewer overflows (SSO)
  Compliance with Federal enforcement action
Notes: Currently there are a number of water issues challenging the state and Hampton Roads. I’ll discuss each of these in further detail and I’ll introduce them briefly here to set the stage for why we were prompted to consider SWIFT.
Chief among them from a state perspective is a rapidly depleting groundwater resource which is not only a threat to the quantity of water supply but also to the quality.
Looking to surface water quality, Chesapeake Bay restoration efforts top the list of challenges. HRSD is on target to meet its nutrient reduction goals but the Hampton Roads region stormwater utilities are faced with costly and complex urban stormwater retrofits. Algal blooms continue to be a concern in the James River and in our local waters. Also, certainly not unique to Virginia, many of our local waters are failing to meet the bacterial water quality criteria for recreational or shellfish use.
Sea level rise is a significant challenge for the Hampton Roads region and this is further compounded by land subsidence.
Our region is also being challenged to reduce wet weather capacity related overflows as part of a federal consent decree.

## Slide 4: Current state of wastewater in Hampton Roads
HRSD costs are rising to treat water to higher standards. Treated water currently discharged to area waterways – no beneficial use.
AQUIFER
OCEAN
SURFACE WATER 80%
GROUND WATER 20%

## Slide 5
HRSD’s Vision for Managed Aquifer Recharge in Eastern Virginia
Notes: The title Master is a blank slide with no graphics so you aren’t locked in to type boxes or a particular layout.
PLEASE NOTE: Slide numbers are on the Master pages, and can be turned on-off by selecting “Header and Footer” from the VIEW menu.
Slide numbering begins on the first content slide, and the title slide has no number.

## Slide 6: SWIFT – Sustainable Water Initiative for Tomorrow
Treat water to meet drinking water standards and replenish the aquifer with clean water to:
  Provide regulatory stability for wastewater treatment
  Provide a sustainable supply of groundwater
  Reduce nutrient discharges to the Bay
  Reduce the rate of land subsidence
AQUIFER
Ocean
Advanced Water Treatment
SWIFT H2O
Notes: Need to break the aquifer mining cycle by adding an advanced water treatment plant at our existing plants sites and injecting that clean water back into the aquifer

## Slide 7: The Challenges/Opportunities for HRSD
~$750M in Nutrient Removal Upgrades by 2021.
  Sidestream treatment: anammox/deammonification & struvite recovery
  More sophisticated mainstream process controls
Biosolids – strong reliance on old Multiple Hearth Incinerators
  Thermal hydrolysis and centralized digestion
~$2.2B in Consent Decreed Mandated Upgrades to Reduce Sanitary Sewer Overflows over 20 years
  Integrated plan to do SWIFT first – Submitted to EPA in October 2017
SWIFT = very large managed aquifer recharge effort pending
  Advanced Water Treatment based on Ozone/Biofiltration/GAC/UV
  ~120 MGD; ~$1B

## Slide 8: De Facto water recycling
Common throughout the world and in Virginia
  James River
  Shenandoah
  Potomac
  Roanoke River Basin (Lake Gaston)

## Slide 9: Water recycling opportunities
Treatment Plant Effluent
Notes: Non-potable – lost YR refinery, have tried to make several other projects work – business case associated with scalping plant for industrial reuse is tough

## Slide 10: Operational Potable Reuse Cases
Project | Location | Type of Potable Reuse | Year | Capacity | Current Advanced Treatment Process
Montebello Forebay, CA | Coastal | GW recharge via spreading basins | 1962 | 44 mgd | GMF + Cl2 + SAT (spreading basins)
Windhoek, Namibia | Inland | Direct potable reuse | 1968 | 5.5 mgd | O3 + Coag + DAF + GMF + O3/H2O2 + BAC + GAC + UF + Cl2 (process as of 2002)
UOSA, VA | Inland | Surface water augmentation | 1978 | 54 mgd | Lime + GMF + GAC + Cl2
Hueco Bolson, El Paso, TX | Inland | GW recharge via direct injection and spreading basins | 1985 | 10 mgd | Lime + GMF + Ozone + GAC + Cl2
Clayton County, GA | Inland | Surface water augmentation | 1985 | 18 mgd | Cl2 + UV disinfection + SAT (wetlands)
West Basin, El Segundo, CA | Coastal | GW recharge via direct injection | 1993 | 12.5 mgd | MF + RO + UVAOP
Scottsdale, AZ | Inland | GW recharge via direct injection | 1999 | 20 mgd | MF + RO + Cl2
Gwinnett County, GA | Inland | Surface water augmentation | 2000 | 60 mgd | Coag/floc/sed + UF + Ozone + GAC + Ozone
NEWater, Singapore | Coastal | Surface water augmentation | 2000 | 146 mgd (5 plants) | MF + RO + UV disinfection
Los Alamitos, CA | Coastal | GW recharge via direct injection | 2006 | 3.0 mgd | MF + RO + UV disinfection
Chino GW Recharge, CA | Inland | GW recharge via spreading basins | 2007 | 18 mgd | GMF + Cl2 + SAT (spreading basins)
GWRS, Orange County, CA | Coastal | GW recharge via direct injection and spreading basins | 2008 | 70 mgd | MF + RO + UVAOP + SAT (spreading basins for a portion of the flow)
Queensland, Australia | Coastal | Surface water augmentation | 2009 | 66 mgd via three plants | MF + RO + UVAOP
Arapahoe County, CO | Inland | GW recharge via spreading | 2009 | 9 mgd | SAT (via RBF) + RO + UVAOP
Loudoun County, VA | Inland | Surface water augmentation | 2009 | 11 mgd | MBR + GAC + UV
Big Spring (Wichita Falls), TX | Inland | Direct potable reuse through raw water blending | 2013 | 1.8 mgd | MF + RO + UVAOP
Notes: Highlight direct potable – Namibia and Big Spring
Yellow is direct aquifer injection – not distribution of techs
Red is VA
Not a full list – other global examples

## Slide 11: Water recycling - Surface water augmentation
Examples:
  Upper Occoquan Service Authority – Northern VA
  Gwinnett County (Georgia)
  Singapore NEWater

## Slide 12: Water recycling - Groundwater recharge via direct injection
Examples:
  Groundwater Replenishment System (Orange County, CA)
  West Basin (El Segundo, CA)
  Los Alamitos (Long Beach, CA)
  Scottsdale Water Campus (AZ)
  Hueco Bolson (El Paso, TX)
+WTP
Notes: Must move the important drinking WTP elements into the AWTP – reorder and make logical process sequence – providing same level of tmt

## Slide 13
SWIFT Research Center (3.8 MLD AWT + recharge well + monitoring wells +
public outreach and education center + research facilities)

## Slide 14
SWIFT Research Center at HRSD Nansemond Treatment Plant (30 MGD)

## Slide 15: Nansemond Plant Schematic

## Slide 16: Process Flow Diagram for SWIFT Research Center

## Slide 17: 1,4-Dioxane
Trace organic included on the EPA Contaminant Candidate List 3
CA Drinking Water Notification Limit = 1 µg/L
  Partial removal by hydroxyl radical through ozonation
  Biodegraded in biologically active filters (some)
  Adsorption on virgin GAC

## Slide 18
Installation of Extensometer to monitor impact on land subsidence
  Operational as of March 2018
  $1M in partnership with USGS and Virginia

## Slide 19: Technology Implementation at HRSD is Driven by:
MINIMIZING Resource Utilization:
  Energy
  Chemicals
  Labor (operations, maintenance, instrumentation…)
  Concrete, footprint, land area
MAXIMIZING Resource Recovery (business case must be good)
  Water
  P
  N (can’t compete)
  CH4 – biogas (electricity, CNG, etc)
  Heat
  Hydraulic energy
  Chemicals of interest (maybe)
  Biosolids (N, P, organics)
  Etc, etc, etc
Intensification

## Slide 20: Mainstream Treatment
Chart: 
| 499536.57244615391 | 333024.38163076929 | 222728.98717948716 | 139711.81923076921 | 135991.86458536584 | 74242.995726495748 | 70000 | 135991.86458536584
Conventional Technologies | 4.689 | 9.378 | 9.7716 | 11.8301 | 16.6871 | 20.4962 | 16 | 8
Footprint
Low
Medium
High
Compact
Large
Activated Sludge
MBRs
IFAS
Life Cycle Cost
$ / Kg N Removed
BAFs
MLE +
Post Denit
Lagoons
Granular

## Slide 21: Mainstream Treatment - Intensified
Chart: 
| 499536.57244615391 | 333024.38163076929 | 222728.98717948716 | 139711.81923076921 | 135991.86458536584 | 74242.995726495748 | 70000 | 135991.86458536584
Conventional Technologies | 4.689 | 9.378 | 9.7716 | 11.8301 | 16.6871 | 20.4962 | 16 | 8
Footprint
Low
Medium
High
Compact
Large
Activated Sludge
MBRs
IFAS
Life Cycle Cost
$ / Kg N Removed
BAFs
MLE +
Post Denit
Lagoons
Granular

## Slide 22: Technology Implementation at HRSD is Driven by:
MINIMIZING Resource Utilization:
  Energy
  Chemicals
  Labor (operations, maintenance, instrumentation…)
  Concrete, footprint, land area
MAXIMIZING Resource Recovery (business case must be good)
  Water (SWIFT)
  P (struvite)
  N (hard to compete with Haber-Bosch right now…)
  CH4 – biogas (electricity, CNG, etc)
  Heat
  Hydraulic energy
  Chemicals of interest (maybe)
  Biosolids (N, P, organics)
  Etc, etc, etc
Intensification

## Slide 23: HRSD York River Plant (15 MGD) First full-scale sidestream deammonification process in North America – partial nitritation + anammox
DEMON

## Slide 24: Drivers for Mainstream Shortcut N Removal
Eliminate External Carbon
Energy
  decreases aeration demand for N removal
  decreases aerobic COD oxidation
  diverts wastewater carbon to anaerobic digestion
Intensification
  carbon diversion = much smaller aeration tank volume required

## Slide 25: Challenges
Management of populations
NOB out-selection (maximize AOB rate)
Anammox retention

## Slide 26: HRSD Chesapeake-Elizabeth BNR Pilot Facility

## Slide 28
Bioaugmentation of sidestream anammox granules
Settling Column for Anammox Retention
Column RAS
Partial Denitrification/
Anammox MBBR
Glycerol
Addition
A-stage WAS Fermentation

## Slide 29
SWIFTVA.COM
cbott@hrsd.com
Notes: This slide can be last so there is something on the screen while the speaker answers questions

## Slide 32
50’
400’
450’
500’
MW-SAT
MW-UPA
MW-MPA
MW-LPA
MAR Well TW-1
~3 days travel time
8+ months travel time

## Slide 33: 5-Stage Bardenpho Configuration
Notes: Summer Operations
  5-stage mode
  3,000 mg/L MLSS in summer
  Carbon addition: 1st stage and 2nd stage anoxic zones
Transition before wastewater temperature is below 17 ⁰C
Historically around December

## Slide 34: Integrated Plan Prioritizes the Greatest Water Quality and Economic Benefits for the Region
Plan Approval
2019
SWIFT
(~$1B)
2030
High Priority RWWMP Projects
(~$200 M)
Final Measures Plan
Pathogen Tracking Program
($10M)

## Slide 35: Impact on nutrient reductions
Chart: Total Nitrogen, (lbs/yr)
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
James River Basin Total Nitrogen | 5944978.0994 | 5319653.9278 | 5353992.616 | 5388752.0661 | 4734866.8849 | 4770184.8677 | 4384767.6351 | 4208201.2161 | 4356489.4797 | 4313638.373 | 4334455.1044 | 2866566.1242 | 2880501.8232
2011 WLA | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000 | 6000000
2017 WLA | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000 | 4400000
Projected 2022 WLA | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000 | 3400000
EPA Backstop | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000 | 1600000
SWR Projected | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
6,000,000 lbs TN
2011 WLA
4,553,500 lbs TN
2017 WLA
3,553,500 lbs TN
2022 WLA
1,600,000 lbs TN
EPA Backstop
Army Base Completed
VIP Completed
Nansemond Completed
James River Completed
Chesapeake-Elizabeth Offline
WLA – Nutrient Waste Load Allocation in lbs/yr
SWIFT Projected TN
James River Basin – TN Similar results with TP and TSS and in other river basins.

## Slide 36: Benefit – Eliminated Costly Urban Stormwater Nutrient BMPs
Executed nutrient trading agreements with 11 MS4 localities
Example – James River TN
3,000,000 lbs/yr TN credit available with SWIFT
64,000 lbs/yr TN removal needed for all stormwater MS4s in James River watershed

## Slide 37: Ammonia-Based Aeration Control (ABAC)
Taking advantage of unused aeration tank capacity!

## Slide 38: Benefits of ABAC
    Reduce energy consumption
      less NH4 converted, aerating at lower DO, less COD oxidized aerobically
    Improve usage of sbCOD, reduce need for supplemental carbon
    Decrease ALK demand
    Decrease chlorine demand – chloramination
    Control ammonia peaks
    Increase in nitrogen removal via simultaneous nitrification/denitrification (SND)

## Slide 39: Upgrading to 5-stage BNR  VIP + 2

## Slide 40: Advancing Process Control: Beyond PIDs…
Supplemental Carbon Control – Feedforward w/ PID control
Chart: Flow (MGD)
Chart: NOX (mg/L)
Notes: Real-time control strategies in place respond to disturbances rather than preventing them. They do a pretty good job when trying to meet effluent nutrient goals. Successful implementation and operation of SWIFT will rely on preventing upsets in the upstream treatment plant and providing optimal stable effluent quality. Adapted PID control from power, chemical and energy industry, which often have much more control over dynamic conditions and economically the drive has pushed them farther forward.

## Slide 41: Advancing Process Control:
White Box - Mathematical Models (ASM equations)
Black Box - Statistical Models
SUMO® 2018.
Multivariate Control (Ge and Song 2013)
Kalman Filtering (Medium 2017)
Artifical Neural Networks (Gomolka et al. 2017)
Notes: Gray-box models combine simplified versions of established mathematical models and statistical methods using real time sensor data to provide more accurate control and prediction of dynamic system demands allowing prevention of upset and increased stability.

## Slide 42: Advancing Process Control: …to Gray-Box Models
White Box
+
Black Box
↓
Gray Box – Combining deterministic models with historical data for new control strategies.
Ali Gagnon,
VT PhD Student
Notes: Gray-box models combine simplified versions of established mathematical models and statistical methods using real time sensor data to provide more accurate control and prediction of dynamic system demands allowing prevention of upset and increased stability.

## Slide 43: Conventional BioP + N Removal
A2/O or Phoredox Process
ANA = Anaerobic
ANX = Anoxic
AER = Aerobic

## Slide 44: “Sidestream BioP” – RAS/Mixed Liquor Fermentation
Tooker, N.B., Barnard, J.L., Bott, C.B., Carson, K., Dombrowski, P.D., Martin, K., McQuarrie, J., Menniti, A., Phillips, H., Schauer, P., Shaw, A., Stevens, G., Takács., I., Onnis-Hayden, A., Gu, A. (2016). Side-stream enhanced biological phosphorus removal as a sustainable and stable approach for removing phosphorus from wastewater. IWA – Nutrient Removal & Recovery, Denver, USA.
Increases reliability of Bio-P when influent VFA is low
Combines hydrolysis, fermentation, and enrichment of PAO
Selection of PAO over GAO
Possibly enrichment of Tetrasphaera over Accumulibacter

## Slide 45: Sidestream Bio-P
Ferment for 24-48 hours without external carbon
More realistic sizing is 4-8 hr HRT with some external carbon addition

## Slide 47: Atlantic Treatment Plant (200 MLD)

## Slide 48: CAMBI Thermal Hydrolysis Process

## Slide 49: Motivation for THP at Atlantic Plant
Class A (with certainty)
  Land Application
  Marketable products
High quality, low odor
Improve dewaterability
  Storage at plant (or field)
  Stackability
Regionalize on anaerobic digestion (intensification)
FOG and high strength waste co-digestion  Energy