## General Steps
Resources
|  | SLAC.M | SLAC.E | JLAB.M | JLAB.E
0.3
1.5
1
1
0.2
|  | 2 | 2
1 | Mobile Pumping Station, weather protection may be necessary for pumping of outdoor components
2 | Handheld Dew point monitor
3 | Helium Cylinder with Grade 4.5 for filling?
4 | Facility Power Available
5 | Dry N2 Cylinder Available
General Steps - Common to All Subsystems
Installation complete & signed
Electrical Pre-Check for Availability
Electrical LOTO complete
Sequential Electrical Power ON Checks
Electrical feed for subsystem under commissioning
Other subsystem 'NOT under commissioning' must be secured
1. Electrical incoming feed for subsystem under commissioning
2. Visual inspection, testing, measuring etc.
Control System - Local - Startup & Check
Control System - Remote - Start up & Check
Sensors, Gauges, Transmitter - Check
1. Checks of HMI
2. Signal Communications
1. Checks of EPICS Screens
2. Signal Communications
3. Data Logging
1. Good Read outs
1. Electrical Commissioning
2. I&C
Commissioning
Purging the subsystem
Filling the subsystem
1. Ensure all connections before evacuation
2. Purging up to ~10-1 mbar
1. Filling with Dry N2 up to 1 ATM
2. Final Filling with GHe up to 1 ATM.
3. System Clean-Up
Pressure System LOTO
Valve Operation Checking
1. Possible after commissioning of Air Compressor and Air Distribution
4. Valve Operation
Heater Operation Checking
1. Ensure Electrical LOTO
5. Heater Operation

## Auxiliaries
|  | Urgency | Duration
Weeks
4
1
1
2
1
6
|  |  | 4 | Mainly cleanup
Assumptions
1 | one trailor are necessary for the warm tank, one trailor for cool down
2 | LN2 Tank and GN2 Distribution may be required for Pre-COMM system clean up back filling
3 | Continuous flow to the Gas analyser is to be ensured.
1 | 1 PPM Reference Calibration Gas for Analyzer
2 | Gaseous Helium Available
3 | Liquid Nitrogen Available
4 | Facility Cooling Tower Available
Auxiliaries Commissioning
Air Compressors Commissioning
Air Distribution Commissioning
1. Including Wet Reciever, Dryers
2. Ensure HV in propers positions
1. Including Dry Air Reciever and distribution
2. Ensure HV in propers positions
Helium Gas Analyzers Commissioning
1. Standalone checking with calibration gas
Recovery Compressor Commissioning
1. Requires filling of Dirty Helium storage Tank-1/6
2. Ensure Oil Level
3. Ensure Adsorber
4. Initial Start-up with bypass only.
Cooling Water Commissioning
2. CP Air Compressors Commissioning
5. Gas Analyzers Commissioning
3. CP Cooling Water System
(79621-0000) Commissioning
4. Recovery Compressor Commissioning
1. HV position as required
2. Filling of water from facility
3. Water Circulation
LN2 Tank Commissioning
1. Nitrogen System Commissioning
1. Ensure System cleanup complete
2. Control Cooling down with external LN2 Tanker
3. Filling of LN2
LN2/GN2 Distribution System Commissioning
He Purifier Commissioning
He Storage Tank Commissioning
6. He Purifier Commissioning
7. He Storage Tank Commissioning
1. Filling of Helium to storage tanks one by one via Recovery System
Vacuum System for Purifier Commissioning
1. Ensure GN2 & LN2
2. HV configuration as required
General Steps Complete

## Helium Compression
|  | Urgency | Duration
Weeks
|  |  | 12 | May be part of Pre-COMM
4
2
1
|  |  | 8 | the Seller shall operate the system under design conditions for a period of 168 continuous clock hours prior to commencement of a 24 hour compressor performance test
Adsorber regeneration (part of 4) may be part of Pre-COMM
5. and 6 together
5.6.7 are all together
1 | Oil Barrel of 55 GAL Available
2 | GHe Cylinder Available
Warm Helium Compression Commissioning
Oil Processor Commissioning
Filling of 300 GAL Storage Vessel
1. Ensure Cold Trap
2. Ensure Regeneration Vacuum Pump
3. Oil Barrel & GHe Supply
4. Pressure LOTO
2. Oil Processor Commissioning
General Steps Complete
Auxiliaries Commissioning Complete
Electrical LOTO
MCC Commissioning
1. Ensure Facility Power for He Compressor
3. MCC Commissioning
Regeneration after Installation before start?
1. Adsorbers Commissioning
1. Ensure All the adsorbers having filled with adsorbents
He Compressor Commissioning one by one from LP - MP - HP
1. Ensure Facility Power for He Compressor
2. Pressure LOTO
3. Electrical LOTO
4. Initial Start-up with bypass flow only
5. Cleanup Compressors system with flow to recovery & purifier
5. He Compressor Commissioning
Oil Removal System Commissioning
6. Oil Removal System Commissioning
1. Ensure All the adsorbers having filled with adsorbents
Oil Management System Commissioning
1. Ensure 40 GAL Oil Vessel
7. Oil Management System
Clean Oil Filling in the He Compressors
1. Use of He Storage Tanks
2. Pressure System LOTO
4. Filling of Oil & Helium
Pure He Filling in the He Compressors
Cleanup Oil Removal System

## 4.5 K Cold Box
|  | Urgency | Duration
Weeks
6
|  |  | 1 | Necessary for Turbines, Vacuum pumps
In service leak test - GC.
|  |  | 2 | Parallel pumping for UCB and LCB
Leak test - delay
|  |  | 4 | May be part of Pre-COMM
Check for cleanup procedure with the actual Turbine P&ID.
|  |  | 3 | Including necessary adjustment in the varibale brakes for the Turbines
|  |  | 0 | In parallel with 5.
|  |  | 5 | Including 4.5 K Cold Box performance, 6 modes of operation considered
NOTE:
1 | Detailed commissioning plan from Vendor is necessary
2 | Detailed schedule and duration of commissioning from Vendor is necessary
4.5 K Cold Box Commissioning (JLAB Pre-check + Vendor)
Filling of Water from Facility Cooling Towers
Secondary Cooling Water Loop Commissioning
1. Pressure LOTO
Upper CB Vaccum System Commissioning
1. Ensure Cooling water supply
2. UCB and LCB Evacuation at room temperature
1. Secondary Cooling Water Loop Commissioning
2. Insulation Vacuum System Commissioning
General Steps Complete
Auxiliaries Commissioning Complete
He Compression Commissioning Complete
Lower CB Vaccum System Commissioning
80 K Adsorber Commissioning
1. Pressure LOTO
3. Adsorbers Commissioning
20 K Adsorber Commissioning
Pure Helium Filling from Main Compressor Station
4. Helium Filling and Cleanup
1. Ensure, Turbines with a dummy cartridge
UCB- 80 K Stage Commissioning
1. Ensure LN2 Available
2. Ensure GHe for Turbine's gas bearing Available
5. Heat Exchangers, Turbines Commissioning
LCB - Stage wise Heat Exchangers and Turbines Commissioning
Cleanup 4.5 K UCB LCB
1. Return flow goes to Recovery System
2. Cleanup with dummy cartridge
Cleanup 10 kL LHe Dewar
Cleanup 16 kW, 2kW & 35 kW Test Heater Loops
LHe Dewar Commissioning
1. Ensure Liquid Level Detection
6. LHe Dewar Commissioning
16 kW, 2kW & 35 kW Test Heater Commissioning
1. Ensure LN2 Available
2. Ensure GHe for Turbine's gas bearing Available
7. Test Heaters Commissioning & Performance

## 2 K CB & IB
|  | Urgency | Duration
Weeks
|  |  | 2 | May be part of Pre-COMM
We should perfrom the cleanup of Distribution Box and cryomodule, evenif this is not own by JLAB. This cleanup is necessary to safegurad JLAB supplied components.
1
2
add Cooling water testing
1
2
|  |  | 3 | Dummy Cryomodule required and placed at the Interface Box level with U-Tubes by shorting Line A to B?
Pump down curve by ALAT.
1
heater, JT-Valve, Liquid Level in the CM.
Assumptions
1 | If cryogenic distribution system is installed
2 | If all cryomodules are installed
3 | If dummy cryomodule is installed.
4 | Low flow configuration in Cold Compressor using CC-6 was not considered.
5 | Two Interface boxes commissioning will be along with the cooling of connecting cyrolines and distribution box.
6 | Commisssioning of two interface boxes are considered together without any U-Tube operation.
2 K Cold Box Commissioning and Interface Commissioning
Electrical LOTO
Test Heater Commissioning
1. Pressure LOTO
2 K CB Vaccum System Commissioning
1. Ensure Cooling water supply
2. Ensure DP oil
3. 2 K CB Evacuation at room temperature
1. Test Heater Commissioning
2. Insulation Vacuum System Commissioning
General Steps Complete
Auxiliaries Commissioning Complete
He Compression Commissioning Complete
4.5 K CB Commissioning Complete
Guard Vacuum Commissioning
1. Ensure Oil level in pump
2. HV configurations
3. Guard Vacuum Commissioning
Assumptions
1. 4.5 K CB is warmed up to room temperature
2. Test Heaters 4.5 K CB are removed
3. 4.5 K CB is configured by connecting Interface CAN and 2 K CB
Pure Helium Filling from Main Compressor Station
1. Helium Filling and Cleanup
1. Ensure, CC bypassed
2. Dummy: Mounting Casing and flange for shiping
Cleanup Cryolines
1. Return flow goes to Recovery System
Cleanup 2 K CB
1. Using CC bypass
2 K Cold Box Commissioning (JLAB Pre-check + Vendor)
Magnetic Bearing Tuning for CC
1. Ensure Cooling water supply
2. Ensure DP oil
3. 2 K CB Evacuation at room temperature
4. Magnetic Bearing Tuning for CC
Cold Compressors Commissioning
1. Ensure flow from 10 kL Dewar
5. Cold Compressors Commissioning+ CB
Interface
A CAN + Dummy CM Commissioning
1. Ensure Cryomodules are bypassed
1. A CAN + Dummy CM Commissioning
Cleanup Dummy
CM, if any