## Slide 1: 2023 StayTreat
PSS Upgrades and Path to one Cert/Year
Jerry Kowal

## Slide 2: Path to One Cert per Year
Legal requirements
Engineering Standards
Certification Frequency Assessment (Proof Test Interval)
How to extend Proof Test Interval
Proposed PSS improvements
PSS Upgrade status
Timeline

## Slide 3: Proof Test Intervals requirements
DOE O 420.2D (Safety of Accelerator Facilities)
  Safety Assessment Document
  Accelerator Safety Envelope
  Credited Controls
  Configuration Management
  Training
  Procedures
FSAD, Rev 8c (Final Safety Assessment Document)
  “All aspects of PSS functionality are certified annually. Certification involves multiday procedure-driven process performed by Accelerator Operation and SSG staff which verifies the functionality of all PSS devices and tests the functionality of all PSS segments as well as the entire system function as a whole.”
  Surveillance Rationale: The PSS design and the maintenance procedures assure the performance and reliability of these systems between certifications.
  Monitoring, testing, calibration and certification requirements for the PSS are based on a comprehensive reliability analysis of the subsystems and components that is included in the PSS design and configuration management processes.
ASE, Rev 9 (Accelerator Safety Envelope)
  “The CEBAF PSS shall be certified annually”
Beam Containment and Access Control Policy, Rev 1.1
  “The PSS hardware and any related software shall be designed, operated, and maintained consistent with applicable Department of Energy (DOE), American National Standards Institute (ANSI), and International Electrotechnical Commission (IEC) standards for industrial safety systems”.
  “The PSS and its components shall provide a level of safety such that likelihood of serious non-recoverable injury to people from prompt ionizing radiation is less than 1 in 10,000 during the operational life of the facility.”

## Slide 4: Proof Test Intervals requirements
IEC 61508
  Functional Safety of E/E/PE Safety-Related Systems
  IEC 61508 is a top-down complete safety lifecycle engineering standard for the design, documentation, verification, validation, commissioning, operation, maintenance and decommissioning of electro-mechanical safety systems.
  Uses a probabilistic/risk-based approach to manage acute risks, with a graded approach requiring higher levels of effort for higher safety risks.
  Includes prescriptive workflows, requirements, check lists, tools and techniques for managing systematic errors and evaluating systematic capability.
  Calculation of Proof Test intervals is a mandatory component of IEC 61508
IEC 61511 (ANSI/ISA-84.00.01-2004 Part 1)
  Functional Safety: Safety Instrumented Systems for the Process Industry Sector - Part 1: Framework, Definitions, System, Hardware and Software Requirements
About 2 dozen relevant IEC Standards

## Slide 5: Proof Test Interval calculation
IEC 61508:
  “Periodic test performed to detect dangerous hidden failures in a safety-related system so that, if necessary, a repair can restore the system to an “as new” condition or as close as practical to this condition”
Example of calculation for safety function comprising a single element:
  is the probability of failure on demand
  is the dangerous undetected failure rate per hour
  is the proof test frequency
Example of calculation for a single channel in 1oo2 architecture:
_

## Slide 6: Proof Test Interval calculation
Reliability of hardware
  Frequency of Certification/Proof Test is directly related to reliability of the system (higher reliability = less frequent Certification)
  Increasing periods between Certification/Proof Tests implies that the hardware channels need to be more reliable to maintain the same level of safety
Chart: Short Proof Testing vs PFD
| 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5
PFD1 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0
Chart: Long Proof Testing vs PFD
| 0 | 2 | 2 | 4 | 4 | 5
PFD | 0 | 0.009 | 0 | 0.009 | 0 | 0.004
Chart: High Reliability
| 0 | 2 | 2 | 4 | 4 | 5
PFD | 0 | 0.004 | 0 | 0.004 | 0 | 0.002

## Slide 7: Proof Test Interval calculation
Proof Test coverage
  Are Proof Tests capable of detecting 100% of failures?
Diagnostic coverage
  Automatic detection of failures
  Ratio of detected dangerous failures to total dangerous failures
  Desired to be at 90% or better (>99% considered high)
DC | Classification
<60 % | none
60% to < 90 % | low
90% to < 99 % | medium
> 99 % | high
Chart: Proof Test Coverage vs PFD
| 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5
PFD1 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0 | 0.004 | 0
PFD2 | 0 | 0.004 | 0.001 | 0.005 | 0.002 | 0.006 | 0.003 | 0.007 | 0.004 | 0.008 | 0.005

## Slide 8: PSS Upgrades – proposed implementation (2019 slide)
Upgrade hardware
  Replace PLCs controllers - Siemens Safety-Rated PLCs
  Redesign interfaces to other system (RF, Box Supplies, Gun, etc.)
  Review other components
Expand the PSS System architecture from 1oo2 to 1oo2D
  Install fiber-optic links between the Systems A and B
  Retain galvanic isolation between the chains
  Utilizes a standard safety rated communication protocol
Implement diagnostic in the software
  Real time detection of failures
  Comprehensive alarming and messaging results in reduced troubleshooting effort
Evaluate the Diagnostic Coverage and Reliability
  Quantify effects of implemented improvements
  Establish absolute reliability - FMEDA (long term effort)
Update Certification procedures and frequency
  Eliminate tests replaced by diagnostic coverage
  Add Fault Insertion Tests as necessary (software testing method deliberately injecting faults)
  Consider Tests staggering and gradation

## Slide 9: PSS Upgrade status
Segments with upgraded PLC hardware & software:
  Injector
  North Linac
  South Linac (SAD23)
  Hall A
  Hall B
  Hall D (SAD23)
  Tagger (SAD23)
Segments awaiting PLC hardware upgrade (SAD24):
  BSY
  Hall C
Other components
  OPS/SSO HMI interface – improved but needs an upgrade
  Light barriers at exit doors, (only X1 upgraded, hardware available)
  Lighting contactors (hardware available)
  Other “ancient” field hardware awaits evaluation and replacement

## Slide 10: Timeline

## Slide 11: PSS Upgrade status – other subsystems
PSS BCM
  Provides protection for Beam Stoppers
  Replacement of obsolete hardware
  Lacks diagnostics and good interface to EPICS and OPS HMI
  Development for UITF started in 2018/2019 but then stopped
Kicker Controls
  Magnet upgraded
  Replacement of obsolete hardware
  Needs a COTS controls if possible
Power Supplies and DC UPS upgrade
  Replacement of obsolete hardware
  Increased reliability
BELS
  “Defense in depth” system
  Replacement of obsolete PLC hardware
  Complex implementation
Video system
  SSO tool for Access Control
  Replacement of obsolete hardware (already procured)
  Moving to IP based, PoE type hardware

## Slide 12: Other related upgrades
Other facilities
  LERF
  CMTF
  VTA
Other associated systems
  Halls ABC ODH
  LERF ODH
  CMTF ODH
  Development & build of next gen Portable Units
  CHL 1&2 ODH
  ESR ODH
  CTF ODH
  HDR ODH

## Slide 13: Questions?

## Slide 14: Architecture of the old system

## Slide 15: Architecture of the upgraded system

## Slide 16: Bonus slides – major terms (mssafety.com)
Functional Safety
  Functional Safety is a term used to describe the safety system that is dependent on the correct functioning of the logic solver, sensors, and final elements to achieve a desired risk reduction level. Functional Safety is achieved when every safety function is successfully carried out and the process risk is reduced to the desired level.
Safety Instrumented System (SIS)
  A Safety Instrumented System is designed to prevent or mitigate hazardous events by taking a process to a safe state when predetermined conditions are violated.”
  “Each SIS has one or more Safety Instrumented Functions (SIF). To perform its function, a SIF loop has a combination of logic solver(s), sensor(s), and final element(s). Every SIF within a SIS will have a SIL level.
Safety Integrity Level (SIL)
  A SIL is a measure of safety system performance, in terms of probability of failure on demand (PFD). This convention was chosen based on the numbers: it is easier to express the probability of failure rather than that of proper performance (e.g., 1 in 100,000 vs. 99,999 in 100,000).
  There are four discrete integrity levels associated with SIL: SIL 1, SIL 2, SIL 3, and SIL 4. The higher the SIL level, the higher the associated safety level, and the lower probability that a system will fail to perform properly.”
  SIL levels apply to safety functions and safety systems (SIFs and SISs).

## Slide 17: FMEDA (Failure Modes Effects and Diagnostic Analysis)
FMEDA is a methodology for the detailed determination of failure causes and their Impact on the system. Evaluates:
  All components of a design,
  The functionality of each component,
  The failure modes of each component,
  The effect of each component failure mode on the product functionality,
  The ability of any automatic diagnostics to detect the failure,
  The design strength (de-rating, safety factors) and
  The operational profile (environmental stress factors).