## Slide 1: Radiation Shielding Design Analysis for the Ring to Second Target Beam Transport at the Spallation Neutron Source Second Target Station
Wouter C. de Wet, PhD
dewetwc@ornl.gov
Accelerator Design and Technology
19 March 2024

## Slide 2: Outline
Introduction to Second Target Station Project - RTST
Shielding Design Guidance
Radiation Transport Methodology
Analysis 1: Truck Access Tunnel & Labyrinth
Analysis 2: HVAC Ducts
Analysis 3: Soil Berm and Electrical Chases

## Slide 3: STS-RTST Overview
RTST - Ring to Second Target Beam Transport
Beam Power is 700 kW (15 Hz)
Proton Energy is 1.3 GeV
Total Length is ~220 m
56 Quadrupole Magnets
15 Dipole Magnets
STS Accelerator Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air
RTBT Leg 1
RTBT Leg 2
Accumulator Ring
First Target Station
PPU Stub
STS Target Building
RTST Truck Access Tunnel & Labyrinth
RTST Straightaway:
CSB Chases
Soil Berm Height
HVAC System
RTST
2.7 MW
2.0 MW
0.7 MW

## Slide 4: Shielding Design Guidance
Dose rates in generally occupied regions should be <0.25 mrem/hr during normal operations
Requirement begins 30 cm from shielding surface
Exceptions possible for regions in which continuous occupation not plausible

## Slide 5: Radiation Transport Methodology
Geometry (CSG, Uns. Mesh, etc.)
Source
Tallies (Flux, Dose, etc.)
Transport Model
Variance Reduction
Radiation Transport Code (MCNP, PHITS, HZETRN, etc.)
Results
Time
Cleverly implemented variance reduction techniques can greatly reduce the amount of time required. In this work, a variety of techniques are implemented, including DXTRAN Spheres and Weight Windows generated using the ADVANTG code.
In the case of “Monte Carlo” transport, increasing simulation run times reduces uncertainty in results.
In this work, all reported results are obtained using the MCNP6.2 radiation transport code.

## Slide 6: Transport Sources
Linear beam losses along active transport lines
  Assume 1 W/m of beam
  1.3 GeV protons
  Lost protons placed in beam tube walls
Backscatter from primary beam
  700kW primary beam on tungsten target
  1.3 GeV protons
Plan View: Proton Flux in RTST Tunnel

## Slide 7: Transport Tallies
MCNP6 TMESH
  25 cm rectilinear mesh
3 Particle Species
  Protons
  Neutron
  Photons
Quantities
  Flux
  Dose Rate
  Exposure contributions calculated via whole-body external exposure effective dose rate flux-to-dose conversion factors.

## Slide 8: Analysis 1
Truck Access Tunnel & Labyrinth

## Slide 9: Truck Access Tunnel
Source: 1 W/m beam losses in RTBT, RTST, and 1 MW primary beam-on-target backscatter.
Region: RTST Truck Access Tunnel and Labyrinth.
Objective Determine if dose rates in occupied regions outside of Truck Access Tunnel and Labyrinth are <0.25 mrem/hr during normal operations.
STS Accelerator Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 10: Truck Access Tunnel Continued
Soil, ρbulk = 1.931g/cm3, (21% H2O content)
Concrete, ρ = 2.339 g/cm3
Steel, ρ = 7.039 g/cm3
Air, ρ = 0.0011988 g/cm3
Elevation View 1 Slice is perpendicular to the truck access tunnel centerline and parallel with the interior face of the stacked steel shielding.
  Slice is intentionally placed in the gap between the exterior wall of the truck access tunnel and interior face of the stacked steel shielding mass.
Elevation View 2 Slice is directly along the truck access tunnel centerline.
Material Specifications
Elevation Views
Elevation View 1 Slice
Elevation View 2 Slice
Plan View 1: Truck Access Region Geometry
Truck Access Tunnel
Concrete Shielding
(CSB-side)
Concrete Shielding
(labyrinth-side)
Labyrinth
RTST
Generally Accessible Room
Generally Accessible Room
Stacked Steel Shielding Blocks
HVAC Ducts

## Slide 11: Elevation View 1, Concrete Shielding & Lintel
b
e
a
f
g
c
d
(CSB-side)
(labyrinth side)
h
Concrete inner walls are equidistant from the steel shielding centerline. In other words, midpoint of c lies directly along the truck access tunnel centerline.
Gap h is not necessary. It may be filled by increasing a to match g. It may not be removed by decreasing g to match a.
Notes
(CSB-side)
(labyrinth-side)
Location of Elevation Slice
Plan View
Elevation View 1: Geometry
Elevation View 1: Total Dose Rate (1W/m Beam Losses & Target Backscatter)
Soil
Concrete (HD)
Concrete
Steel 1020
Air
Excess volume to be trimmed
a
b
c
d
e
f
g
528.3 cm
110.0 cm
538.32 cm
733.32 cm
85.0 cm
30.5 cm
537.3 cm
Dimension(s)
Height of concrete shielding from tunnel floor.
Required width of concrete shielding (CSB-side).
Interior spacing between concrete shield walls.
Full width of concrete lintel (outer concrete extents).
Required width of concrete shielding (labyrinth-side).
Height of concrete lintel.
Concrete lintel distance from tunnel floor.
h
9.0 cm
Vertical gap between concrete lintel and walls.

## Slide 12: Elevation View 2, Steel Shielding Centerline & Lintel
There is no gap between the underside of the stacked steel shielding blocks and the tunnel floor/road elevation. Blocks will sit directly on the ground.
Dose rates streaming through HVAC ducts exceeding 0.25 mrem/hr on left side of plots are for the first design iteration and are no longer relevant.
Notes
Elevation View 2: Geometry
Elevation View 2: Total Dose Rate (1W/m Beam Losses & Target Backscatter)
j
i
k
l
m
Chart: Steel Shielding Dose Rate vs. Depth
(CSB-side)
(labyrinth-side)
Plan View
Location of Elevation Slice
Soil
Concrete (HD)
Concrete
Steel 1020
Air
i
j
k
l
m
30.5 cm
245.0 cm
528.3 cm
9.0 cm
9.0 cm
Concrete lintel depth.
Required depth of stacked steel shielding.
Height of stacked steel shielding.
Gap between truck access tunnel exterior wall and interior face of stacked steel shielding blocks.
Gap between concrete lintel and stacked steel shielding.

## Slide 13: Plan View 1, Truck Access Shielding & Labyrinth
Plan View 1: Geometry
Plan View 1: Total Dose Rate (1W/m Beam Losses & Target Backscatter)
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 14: Plan View 1, Truck Access Shielding & Labyrinth
Plan View 1: Geometry
Plan View 1: Geometry
o
3
1
2
y
q
n
u
v
z
x
t
w
p
r
s
Soil
Concrete (HD)
Concrete
Steel 1020
Air
Excess volume to be trimmed
n
o
p
q
r
s
t
60.96 cm
528.3 cm
452.12 cm
20.32 cm
452.12 cm
208.28 cm
279.4 cm
Dimension(s)
Truck Access Tunnel outer concrete wall thickness.
Width of stacked steel shielding blocks. Does not include the 5.0 cm gaps on either side between the interior faces of concrete shielding walls and steel mass.
Length of first hallway in Truck Access Tunnel labyrinth (width is 147.32 cm).
Truck Access Tunnel labyrinth concrete wall thickness surrounding inner soil shielding mass.
Length of second hallway in Truck Access Tunnel labyrinth (width is 152.4 cm).
Truck Access Tunnel labyrinth inner soil shielding mass thickness in the dimension perpendicular to the Truck Access Tunnel centerline.
Truck Access Tunnel labyrinth inner soil shielding mass thickness in the dimension parallel to the Truck Access Tunnel centerline.
u
55.88 cm
Truck Access Tunnel concrete wall thickness.
v
w
x
y
152.4 cm
55.88 cm
20.32 cm
883.92 cm
Width of third hallway in Truck Access Tunnel labyrinth.
Truck Access Tunnel labyrinth concrete wall thickness.
Truck Access Tunnel labyrinth interior concrete wall thickness.
Length of third hallway in Truck Access Tunnel labyrinth.
z
1
2
3
55.88 cm
5.0 cm
5.0 cm
9.0 cm
Truck Access Tunnel labyrinth concrete wall thickness.
Gap between concrete shielding wall (CSB-side) and and stacked steel shielding mass.
Gap between concrete shielding wall (labyrinth-side) and and stacked steel shielding mass.
Gap between stacked steel shielding blocks and Truck Access Tunnel outer wall.

## Slide 15: Analysis 2
HVAC Supply and Return Ducting

## Slide 16: HVAC Supply and Return Ducting
Source: 1 W/m beam losses in RTBT, RTST, and 1 MW primary beam-on-target backscatter.
Region: HVAC ducts just upstream of the beam-right bend between CSB and RTST Truck Access Tunnel.
Objective Determine if dose rates in occupied regions on berm surface outside HVAC ducts are <0.25 mrem/hr during normal operations.
STS Accelerator Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 17: HVAC Supply and Return Ducting
STS Accelerator Geometry
Elevation Slice
Total Dose Rate, mrem/hr
Elevation Slice Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 18: HVAC Supply and Return Ducting
STS Accelerator Geometry
Elevation Slice
Total Dose Rate, mrem/hr
Elevation Slice Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 19: Analysis 3
RTST-to-CSB Concrete Chases

## Slide 20: RTST-to-CSB Concrete Chases
Source: 1 W/m beam losses in RTBT, RTST, and 1 MW primary beam-on-target backscatter.
Region: Concrete chases inside the soil berm above the RTST tunnel.
Berm thickness is ~530 cm.
Objective Determine if dose rates in occupied regions on berm surface and inside CSB due to streaming through concrete chases are <0.25 mrem/hr during normal operations.
STS Accelerator Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 21: RTST-to-CSB Concrete Chases
STS Accelerator Geometry
Elevation Slice
Total Dose Rate, mrem/hr
Elevation Slice Geometry
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 22: RTST-to-CSB Concrete Chases
STS Accelerator Geometry
Total Dose Rate, mrem/hr
Elevation Slice Geometry
Elevation Slice
Soil
Concrete (HD)
Concrete
Steel 1020
Air

## Slide 23: Summary
Second Target Station RTST tunnel shielding design includes a multitude of smaller independent designs.
These major component designs are demonstrated to meet their intended shielding design requirements during continuous operation of the RTST beamline:
  Truck Access Tunnel & Labyrinth
  HVAC Ducts
  Soil Berm and Electrical Chases

## Slide 24: Questions?

## Slide 25
Backup Slides

## Slide 26: RTST Geometry

## Slide 27: RTST Geometry (slightly closer)